## Slide 1
POWERNEXT-AI · CPRI WITH MIT BENGALURU · TRACK 1
AI-Driven Optimisation of High-Voltage Impulse Generator Settings
Decision support for 400 kV insulator testing to IEC 60060-1
Team Slayers
Exact circuit physics · learned hall correction · one offline application
Notes: Introduce the team and the track. One line on the idea: physics computes the waveform and the IEC procedure judges it; a learned correction handles what the textbook cannot know about a particular hall.

## Slide 2
Problem statement
Track 1: optimise impulse generator settings for 400 kV insulator testing
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 2
Calculate settings
Fire a trial shot
Read the IEC shape
Adjust: climb up
Standards
Lightning 1.2/50 µs
Switching 250/2500 µs
IEC 60060-1 tolerances on shape, crest and overshoot
Machine
HAEFELY 508085/E
12 stages, 0.125 µF and 200 kV each
Front 30 / 465 / 3700 Ω, tail 520 Ω and 22 kΩ
Objective
Recommend stages, charge, Rf and Rt
Fewer trial shots
Fewer climbs up the generator
Notes: Labs compute settings, fire reduced-voltage trial shots, read the IEC shape and adjust resistors. Every adjustment is physical work on a 2.4 MV generator. CPRI asked for stage count, charging voltage, front and tail resistance, compliant with the lightning and switching standards, with fewer trial shots.

## Slide 3
Solution at a glance
Physics first; learning only where the equations cannot reach
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 3
Inputs and validation
Physics model
Learned hall correction
Ranked settings
Shot loop and memory
Exact circuit physics
Solved by eigendecomposition; IEC evaluation, deterministic
Search over real stock
Every unit and series or parallel pair of units
Learned correction
Calibration, then boosted trees on the residual
Hardware check
Capacitor loading, resistor build, both stocks
Shot loop
Voltage first; a climb only when needed
Hall memory
Four numbers a test, kept in the browser
Notes: The pipeline reads left to right. Validation uses the IEC 60071 table. The target voltage is corrected for the atmosphere. The physics model predicts every stocked setting, the learned correction adjusts the prediction for this hall, and the ranked recommendation comes with a hardware check. After a shot the loop and the hall memory refine the next setting.

## Slide 4
The physics model
A Marx generator reduced to one equivalent stage and solved exactly
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 4
C1
generator
Rf
front resistor
L
loop inductance
C2
load
Rt
tail resistor
Equivalent circuit
C1 = p · C_stage / n, V0 = n · V_charge
Rf = n · Rf_stage / p, Rt = n · Rt_stage / p
L = n · L_stage / p + L_lead
C2 = C_test + 545 + 500 + 150 pF
What the front and tail see
Front: series capacitance Ce = C1·C2 / (C1 + C2), T1 ≈ 3 · Rf · Ce
Tail: both capacitors in parallel, T2 ≈ 0.7 · Rt · (C1 + C2)
12 stages, 90 pF disc string: T1 ≈ 1.2 µs, T2 ≈ 51 µs by hand
Notes: n stages in series and p parallel columns. The circuit is linear, so it is solved by eigendecomposition with no time stepping. The textbook expressions are cross-checks. The nameplate agrees with the physics: Rt per stage = T2 / (0.7 C_stage) gives 571 ohm and the plate says 520.

## Slide 5
How a setting is judged
The IEC 60060-1 procedure, replicated exactly
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 5
±30 %
front time T1, target 1.2 µs
±20 %
tail time T2, target 50 µs
±3 %
crest voltage, both impulse types
≤ 10 %
overshoot, lightning impulse
Switching impulse
Time to peak 250 µs ±20 %, tail 2500 µs ±60 %, crest ±3 %
Tolerance margin
max over the bands of |error| / tolerance. Below 1.0 the setting is inside every band
Notes: The evaluator follows the standard: a fitted double-exponential base curve and the k-factor test-voltage function. Using the circuit's zero-inductance curve instead once made us reject the only compliant settings, so the procedure itself must be replicated. Margin is the worst error divided by its tolerance; below one means inside every band.

## Slide 6
Learning the hall
Calibrate the physics, boost the residual, then set the charge
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 6
1 Calibrate
2 Boost
3 Correct
4 Set the charge
Calibrate
loop inductance, extra inductance, extra capacitance, divider response, one efficiency
Boost
300 trees, depth 3, on the relative residual, from 13 inputs
Correct
prediction = physics × (1 + learned correction); overshoot has its own model
Shot loop
Shape passed: change only the voltage. Otherwise the fewest resistor changes.
Hall memory
Four ratios a test; active from three tests, weight n / (n + 6).
Notes: Calibration fits four effective circuit parameters and one efficiency to the hall's shots. The fitted values are effective: loop inductance and divider response both slow the front and the fit trades one for the other, so the app does not present them as measurements. Boosting learns the relative residual with 300 trees of depth 3. The training shots come from a simulated hall and must be replaced with real ones.

## Slide 7
Inputs: everything CPRI specified
A layman enters a level; an engineer can enter all of it
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 7
✓
Impulse type
lightning or switching
✓
Crest voltage
IEC level, or any kV
✓
Insulator capacitance
measured or inferred
✓
Divider capacitance
default 500 pF
✓
Stray capacitance
default 150 pF
✓
Lead inductance
1 to 120 µH
✓
Front resistor units
tick what exists
✓
Tail resistor units
520 Ω, 22 kΩ
✓
Units per stage
1, 2 or 4
✓
Polarity
positive or negative
✓
Site atmosphere
temperature, humidity, altitude
✓
Equipment and Um
cross-checks the level
Notes: Every item on CPRI's input list can be entered. Resistor availability works over the nameplate units in the browser; any other stock runs in the Python engine, which takes the stock as a parameter.

## Slide 8
Outputs and compliance
Every output on CPRI's list, with the evidence beside it
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 8
✓
Stages and charge
per stage and total
✓
Front and tail resistance
with how to build each
✓
Front, peak, tail time
predicted against target
✓
Crest voltage
predicted, with % deviation
✓
Within or outside limit
tolerance margin and pill
✓
Ranked alternatives
recommended plus two
✓
Target vs predicted
waveform plot per option
✓
Decision summary
one card per request
✓
Hardware check
loading and buildability
Notes: The waveform plot is an idealised double exponential matched to the predicted T1 or Tp and T2, and is labelled as such. The deviation table shows signed percentage error against the target with its band.

## Slide 9
Beyond the brief
What CPRI's reference solution does not include
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 9
Atmospheric correction
IEC 60060-1: Kt = k1 · k2
45 °C, 20 %, 380 m: Kt = 0.914
1550 kV → 1417 kV
Polarity
Positive or negative
v(t) → −v(t): same setting
reverse the charging polarity
Stage connection
2p6s … 6p2s
maximum output (12 / p) × 180 kV
1550 kV needs all 12 in series
Lead inductance
1 to 120 µH, physics at that value
more overshoot, shorter tail
Overshoot warning
predicted ringing from 5 %
physics 0.2 %, hall 8.3 %, app 8.6 %
Wrong-input handling
IEC 60071 level table
capacitance typed in nF caught
Notes: Atmospheric correction changes the target voltage, not the waveform. k2 is a declared approximation because the standard gives it as a graph. Polarity is a sign flip of a linear circuit. Series-parallel connections are physics only. Lead inductance runs the physics at the entered value.

## Slide 10
Safety and buildability
Every recommendation is checked against the capacitors and the available units
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 10
Charge per stage against the 200 kV capacitor rating (1550 kV lightning, 90 pF disc string)
140.9 kV = 70 %
90 % operating limit
100 %
Energy
1.24 kJ of 2.5 kJ per stage; 14.9 kJ of 30 kJ stored
Nameplate stock
single 30 Ω front and 520 Ω tail units: 12 of each
CPRI Excel stock
30 Ω is one unit; 520 Ω = 20 + 100 + 200 + 200 in series
Shot loop and memory
The next charging voltage is capped at 90 % of rating too, and its loading is shown with every next setting.
Notes: The charge is capped at 90 percent of the capacitor rating everywhere and the app shows the loading explicitly. Every recommendation is drawn from stocked units, so it is buildable by construction; the panel shows the recipe and the unit count. CPRI's Excel calculator stock is a second description of equipment: our values can be built from it, while their switching dataset's front values exceed their own inventory.

## Slide 11
Results: less work at the generator
120 simulated sessions, 12 halls, 26 paired tests; unsolved sessions counted at 10 shots
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 11
Resistor changes (climbs) per test, hardest severity
Chart: 
| Black-box AI | Current practice | App with memory | Lab memory
v | 4.72 | 2.1 | 0.48 | 0.38
Compliant on the first shot, hardest severity
Chart: 
| Current practice | Physics calibration | App with memory | Lab memory
v | 28 | 31 | 59 | 62
Easy halls: current practice already succeeds first time (100 %). Simulated halls; real trial shots would settle which severity a real hall is.
Notes: Climbs are Dr. Sheshu's own pain point. At the hardest severity lab memory needs 0.38 climbs a session against the technician's 2.10, and black-box AI without physics is worse than a technician. Paired tests: lab memory climbs p = 0.0007 and app memory p = 0.0004, each surviving the Bonferroni threshold of 0.0019. In a well-characterised hall current practice already works; the gain is where the hall is poorly known.

## Slide 12
Accuracy against CPRI's weighted kNN
Judged on MAPE, MSE and RMSE: two datasets, two different stories
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 12
Simulated hall: front-time error, %
Chart: 
| Textbook | CPRI weighted kNN | Neural network | Gradient boosting | Physics + learned
v | 8.57 | 5.38 | 2.16 | 1.2 | 0.8
CPRI's dataset: front-time MAPE, %
Chart: 
| kNN as shipped (k = 7) | kNN tuned (k = 25) | Ridge | Neural network | Gradient boosting
v | 0.609 | 0.587 | 0.57 | 0.574 | 0.578
Notes: On our simulated hall the residual has physical structure and the hybrid is 6.7 times more accurate than kNN on front time and 6.1 times on larger insulators. That is not evidence about CPRI's data. On CPRI's own dataset the gain is small: Ridge 0.570 against 0.609 for kNN as shipped, and level with their kNN once its k is tuned from 7 to 25. Their synthetic residuals are mostly noise; the best model explains about 40 percent of the front-time residual.

## Slide 13
How CPRI's data is used
Two machines are described; each has its own role
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 13
CPRI Excel calculator machine
HAEFELY 508085/E nameplate machine
3 µF per stage, 15 stages
25 Ω tail per stage; 2000 synthetic rows
0.125 µF per stage, 12 stages
520 Ω tail; from the problem statement, page 4
Used for
benchmark against their kNN; reproduced to four decimals (9 of 9)
Used for
the physics, the search, the learned model and the app
Also from CPRI's workbook
default divider and stray capacitance; the resistor inventory in the hardware check
Notes: CPRI's dataset is generated for the Excel calculator's machine: 3 microfarad per stage, 15 stages, 25 ohm tail per stage. The nameplate machine is 0.125 microfarad, 12 stages, 520 ohm tail. Training on the 3 microfarad rows for the 0.125 microfarad machine would look accurate in a benchmark and be wrong on the generator, so their data is the benchmark against their kNN and the learned model is built for the nameplate machine.

## Slide 14
Verification
Every claim is checked, and the build stops on a mismatch
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 14
88
Python self-checks pass
9 / 9
CPRI kNN metrics reproduced to four decimals
192
browser checks on the finished page
0
mismatches allowed between browser and Python
Circuit 18, waveform 12, atmosphere 14, operator input 35, CPRI kNN 9.
Browser: every equipment, impulse, class and level; wrong inputs; dark mode; phone width.
Notes: Physics is checked against Kuffel's textbook expressions and the IEC procedure. CPRI's kNN is reimplemented and matched to their sheet to four decimals. The app's JavaScript is run in Node against Python's predictions before the page is written. A Playwright run drives the finished page the way a hostile judge would.

## Slide 15
Tools and technology
Open-source stack; no server, no licence, runs offline
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 15
Modelling
Python 3
NumPy, SciPy
pandas
Machine learning
scikit-learn
Gradient boosting, Ridge, kNN, MLP
SciPy least squares
Application
HTML, CSS, JavaScript
No framework, no server
Trees exported to JSON
Standards
IEC 60060-1
IEC 60071
Kuffel, High Voltage Engineering
Testing
Playwright, Chromium
Node.js cross-checks
Paired Wilcoxon tests
Delivery
Git, GitHub
python-pptx, ffmpeg
IBM Plex typeface
Notes: Everything is Python for the modelling and a single self-contained HTML file for the operator application. Boosted trees are trained with scikit-learn and exported to JSON so the browser executes the same model. The page's JavaScript is verified against Python in Node before every build.

## Slide 16
Way forward
What real trial shots from CPRI would unlock
PowerNext-AI · CPRI × MIT Bengaluru · Track 1 · Impulse Generator Settings
Team Slayers | 16
Retrain on real shots
Replace the simulated hall's log with CPRI's measured trial shots
Re-run the benchmark and the paired tests
Confirm the hardware
Resistor units per stage
Loop inductance of the hall
Meaning of the nameplate stage connections
Validate the evaluator
IEC 61083-2 reference waveforms
The standard edition CPRI evaluates against
Open to extend
Test-object failure modelling, other equipment classes, and a shared hall memory across machines
Notes: Real shot records answer the one question the simulator cannot: which severity a real hall is. They would also let the learned correction be retrained on the real machine, and confirm the hardware facts the nameplate does not give.

## Slide 17
Thank you
Impulse Generator Settings · Team Slayers
Offline application, source, benchmark, deck and video:
github.com/Shreyaskale7/Impulse_Twin
PowerNext-AI · CPRI with MIT Bengaluru · Track 1
Notes: Close on the repository and invite questions.